## Slide 1: BTF/LINAC upgrade status
P. Valente
Acc. Div. Meeting, 14 Dec. 2018
Update since Oct. 15
Plans for BTF-2 installation and commissiong
PADME run status
More future activities

## Slide 2: Modulators upgrade

## Slide 3: Modulators upgrade: PFN charging supplies
New TDK-Lambda
junction box
and charging power supplies
PFN Charging Time 10 ms, 40kV 320A
Test of Simulated Remote control and local control
New filament power supply
Self-made cooling system

## Slide 4: Modulators upgrade: PFN charging supplies
New TDK-Lambda power supplies tests OK
(Mod. D)
Up to 150 MW at SLED output
New Thyratron setup
(Mod. B)
Faulty capacitors
(Mod. D and C)

## Slide 5: New modulator construction ongoing

## Slide 6: BTF line splitting

## Slide 7: Experimental hall 2 – new bunker
All concrete blocks delivered
Lateral shielding installed
Bins to be tested under load (January)
Bunker to be completed (January)

## Slide 8: Power supplies
New BTF PS room
  Room 17 and 18 available
  Electricity, conditioning and cooling preparation starting from Dec. 20 (Christmas stop for LINAC/PADME)
  Cable tray ready
  Power cables to be laid down during shutdown
Power supplies
  All power supplies of new magnets delivered yesterday
  Now at MEA
  Quadrupoles PS to be installed in one of our racks
  DHPTB102/DCSTB200 rack to be moved in the new BTF PS room in January
Control test program available
  SAT tests as soon as connected to load

## Slide 9: New magnets

## Slide 10
Sigmaphi has practically completed the construction of DH dipoles
  Working on manifolds
  Delivery expected in January
Delivery of new quadrupoles due in February
Construction drawing

## Slide 11: To do list: new magnets
Magnetic field characterization of:
  2 DC dipoles (delivery Jan. 2019)
  7 quadrupoles (delivery Feb. 2019)

## Slide 12: BTF-2 installation

## Slide 13: To do list
New cooling plant
  Not ready (Order issued)
  Some power can be added using the existing (revised) circuit
  External work can be done with BTF in operation
  Final connection of water pipes requires the facility to be stopped (for a few days)
Installation and alignment of:
  Supports
  2 DC dipoles
  6 quadrupoles
Vacuum
  Pipes (Order issued)
  Valves and pumps
  Scrapers: delivered, being tested
Cabling:
  Power cables, control cables available in Jan. ‘19.
  New iron staircase for passing over the beam-lines: to be designed and ordered
All components should be ready for installation by Mar. 2019
  Time set by the end of PADME run/beginning of DAFNE recommissioning
  Switch on DHPTB102 as soon as possible, validate beam-splitting scheme and timing modifications
  This would allow driving the beam on BTF-2, at least up to the first DH dipole
2-way pipes for DHSTB201 and DHSTB202:
3D designed finalized in May
Detailed drawings to be done

## Slide 14: Open points
Dis-installation procedure of PADME setup, without and with BTF-2 beam-line has to be studied
Authorization for beam in the BTF-2 branch needed also for the commissioning of the partial line staying inside BTF-EH1;
  At least it has to be cleared by RPO (EQ)
  This, together with the PADME setup dis-installation, sets the time scale for re-opening the BTF to the standard users
Option B would drive the beam practically with the same dump configuration as in the original BTF authorization
A: partial BTF-2 installation (now)
B: partial BTF-2 installation with one DH only

## Slide 17: PADME run status

## Slide 18: Long beam-pulse optimization
Improvement of DANE hall shielding
  Limited to 10k positrons/pulse due to RP limit in the hall
    Added concrete (50 cm) in front and lead on the top of the “blue wall”
    Up to 20k positrons/pulse: nominal intensity for 200 ns long pulses (102 positrons/ns density)
Continuous optimization of LINAC
  Transport optimization (focussing coil, LINAC quadrupoles) for reducing the dose in the tunnel
    A lot of work in October: great reduction of lost beam due to defocussing along the LINAC for getting the required intensity at BTF target. Hottest point: three-way vacuum chamber downstream of BTF pulsed 3 dipole
  Optimization of gun HV vs. pulse signal height (new attenuator) vs. grid voltage vs. timing with respect to RF
    From 20k positrons/pulse with approximately 10-12 Sv/h in BTF hall, corresponding to 51010 electrons on BTF target, further improvement by a factor 2 in present configuration
At gun exit
At LINAC end
At BTF target
SLED’ed RF limits the effective pulse length to 200 ns (250 ns at gun)

## Slide 19: Run stability
Generally very stable conditions
LINAC energy fluctuations generally produce (small) changes in the transport, altering both the intensity on PADME and the beam spot position and size
PADME target sees few tens of m of average position variations
Target and average
Intensity at target
Target and size
Photons in SAC

## Slide 20: PADME integrated luminosity
Good physics data since Nov. 1st, 2018
From 10k positrons/pulse to 20k positron/pulse
(shielding)
Trigger board fault
Dec. 2018
Jan. 2019
Feb. 2019
Nov. 2018
Days
Positrons on traget

## Slide 21: ASIF phase 2

## Slide 22: Premesse
ASIF: Progetto sulle infrastrutture per irraggiamento di interesse spaziale di ASI con ENEA e INFN (LNF e LNS, LNL, TIFPA)
Fase 1 (1 anno) completata, circa 1.5M, di cui 60k per LNF
  Adeguamento alle direttive ESA per irraggiamenti (ESCC)
  Attività di studio e caratterizzazione che hanno portato a un vero e proprio run di irraggiamento con un proto-cliente (TRAD)
  Si è dimostrato:
    La fattibilità e la capacità di controllare la dose e l’uniformità
    La necessità di aumentare il flusso a bassa energia e quindi – di fatto – la scarsa utilizzabilità del fascio secondario del linac
Dopo la fase di studio, una fase 2 più operativa
  Possibilità di un maggiore coinvolgimento (e finanziamento) per LNF

## Slide 23: Tempi e taglia del progetto
Definizione del Work Package di LNF nell’ambito di ASIF-2 entro il 15 gennaio ‘19
Firma dell’accordo e partenza del finanziamento e del progetto: marzo-aprile ‘19
Durata: 2 anni
Ordine di grandezza del finanziamento: 0.5M
Electrons irradiation requirements
Fluence: up to 1015 cm-2
Flux: 41015 cm-2 h-1 11012 cm-2 s-1
Energy: 1– 3 MeV
Area: up to 22 cm2, few % uniformity