## Slide 1
Progress Towards the Development of Cooling Demonstrator of the CBM Silicon Tracking System
Kshitij Agarwal, for the CBM Collaboration
Eberhard Karls Universität Tübingen, Tübingen, Germany
Compressed Baryonic Matter experiment at FAIR
CBM aims to explore regions of high-baryonic densities of QCD phase diagram
Requires detection of rare probes
→ 105 – 107 collisions/sec (Au-Au)
→ Momentum Resolution p/p  1-2%
→ High track reconstruction efficiency with
pile-up free track point determination
Silicon Tracking Station: Key to CBM Physics
→ 8 Tracking Stations inside 1Tm field
→ 896 double-sided micro-strip sensors
→ Low Material Budget: 0.3% - 1.5% X0/station
→ Radiation tolerance: ≤ 1014 neq cm-2
→ Signal-to-noise ≥ 10
→ Self-triggering front-end electronics located outside acceptance
→ ∼1.8 million r/o channels + ∼16000 r/o ASICs “STS-XYTER”
CBM Silicon Tracking System
Cooling Demonstrator
Front-End Electronics Cooling
Optimisation of CO2 Operational Parameters
Optimisation of Thermal Interfaces
Conclusion and Outlook
References
Why Bi-Phase CO2 ?
High volumetric HTC  Smaller tubes
Isothermal evaporation
High pressure  Thermal Stability
CO2 Cooling Plant
(TRACI-XL @ GSI - Darmstadt)
Distribution system
Cooling Demonstrator
(2 STS Half-Stations)
Thermal Enclosure
(CF Sandwich)
Cold N2 Flushing
FEE Boards
Read-Out + Power-Out Boards
FEE Cooling Plate (Press-Fitted Tube Channels)
PED Compliant @ 100bars
Front-End Electronics Cooling Concept
J. Heuser et al., Technical Design Report for the CBM Silicon Tracking System (STS) (2013)
E. Lavrik, ‘Development of quality assurance procedures and methods for the CBM Silicon Tracking System’, PhD Thesis, Uni. Tübigen (2017)
B. Verlaat et al., Proceedings of 10th IIR Gustav Lorentzen Conference on Natural Refrigerants (2012), GL-209
Z. Zhang, CERN-THESIS-2015-320 (2015)
M. Rauch, CERN-THESIS-2015-247 (2015)
Ongoing R&D for cooling demonstrator with 2 STS Half-Stations
Bi-Phase CO2 cooling is an optimal solution for cooling the STS electronics
→ T-p v/s L analysis + Thermal FEA model developed to computationally characterise FEE cooling setup
→ Characterization parameters for FEE cooling of first 2 STS Half-Stations with press- fitted tube channels obtained
→ Experimental verification with CO2 needed upon cooling plant completion
→ Thermal interface optimisation shows that using grease increases thermal efficiency
→ Further options (e.g. Graphite tapes etc) will also be studied
Forced N2 cooling on sensors needed to minimise radiation damage
→ Realisitc mechanical setup with minimum material budget inclusion is desired
Thermal characterization of HV-LV, optical etc connectors is foreseen
Operational experiences from mSTS@SIS18 (Aug-Sep‘18) for demonstrator integration
Thermal Interface Materials (TIMs)
→ Increase area of contact & thermal conductivity
Relative measurements with water as coolant
→ Flattening the interfaces (∼10µm) improves the results substantially
→ Good agreement (± 10%) b/w exp. – FEA
Power dissipation ∼40kW in ∼2m3
Sensor temp.
≤ -10°C
Bi-Phase CO2 cooling at -25°C for FEE
Forced N2 cooling directly for sensors
Cooling & Integration Challenges
Sensor cooling with least X0/station
RH << 1% @ 25°C to avoid condensation
High-density feedthroughs, transfer lines
Max. FEE temp. < -10°C 
Thermal FEA
(SolidWorks)
T-p v/s L Analysis
Flow Pattern Map
(MATLAB + REFPROP)
Cooling Demonstrator FEE Operational Parameters |  |  |  | 
TCO2 = -25°C, Tube Deq = 3.6mm (O.D. 6mm), L = 2m |  |  |  | 
Quarter-Station # |  | PFEE (W) | Fr (g/s) | ΔP (bar)
1 | Unit 0 | 265 | 3 | 0.0342
 | Unit 1 | 609.5 | 7 | 0.1127
2 |  |  |  | 
 | Unit 2 | 344.5 | 3 | 0.0459
TIM Optimisation |  |  | 
TH2O = 15°C, Q̇ = 160W, Fr = 11.1g/s |  |  | 
Interface #1 | Interface #2 | Maximum Fin Temp. (°C) | 
 |  | Exp. (PT100) | Thermal FEA
Grease | Grease | 29.7 | 32.0
 | C-Foil | 29.6 | 32.0
C-Foil | Grease | 33.7 | 32.1
 | C-Foil | 33.9 | 32.1
TIM Properties |  |  | 
 | k (W/m∙K) | d (µm) | RѲ (d/k; m2∙K/W)
Grease | 5.0 | 30 | 6.0 x 10-6
C-Foil | 16.0 | 125 | 7.8 x 10-6
STS in Dipole Magnet
Viscous TIM (grease) is better 
FEE shielding works 
FEE Cooling Block with dummy FEB-8 & PT100 sensors
STS Unit 01