## Slide 1: The LHCb Event Builder: an update
Francesco Sborzacchi, I.N.F.N L.N.F./CERN
Workshop sul calcolo nell’ I.N.F.N May 2022

## Slide 2: The LHCb Upgrade 1
100 m underground
30 m long
40 MHz p-p bunch crossing rate
Trigger-less readout
MHz

## Slide 3: LHCb Online Computing 2020+
10 million channels
4 TerabByte/s total data rate
400 Port InfiniBand + 4000 port Ethernet (10/100/200 Gbits) network
170 Readout servers (AMD Rome) with FPGA and GPGPU (A5000)
4000 dual socket servers (AMD/Intel)
60 PB storage

## Slide 4: Increase in data lets system grow…
No additional space nor cooling in the underground facilities
Computing Power needed : 2MW nominal
Space constraints: 5000Us
I/O connectivity @ 14000+ optical fibres

## Slide 5: The Modular DC installation

## Slide 6: Data Processing and Selection
Two stages of software filtering:
  1) "HLT1" on GPGPUs
  2) "HLT2" on CPUs
  Large storage buffer to decouple the two
Calibration and alignment are performed "semi live", while the data are buffered
HLT2 output is offline-ready for “grid” analysis

## Slide 7: System Overview

## Slide 8: Back-end PCIe40
A single custom-made FPGA board for DAQ and Control
Based on Intel Arria10
48x10G-capable transceivers on 8xMPO for up to 48 full-duplex Versatile Links
  478 boards in total
  16x PCIe 3.0

## Slide 9: Event builder server
2 AMD EPYC 7002-series CPUs
3 readout boards
2 InfiniBand 200G NICs
Up to 3 GPUs
512 GiB RAM
PCIe 4.0
8+8 DDR4 channels

## Slide 10: EB Servers Challenges
Memory subsystem pushed to the limits! RDMA is crucial.

## Slide 11: Experiment Control System
SCADA control system based on WinccOA
500 VMs (RHEV cluster)
NetApp AllFlash Nvme storage (NFS)
16 Hypervisors
  16 TiB of Ram
  1024 cores in total
  2x100Gb/s network

## Slide 12: HLT1 Buffer Storage
32 x WD shelves @ 102 disks 14TB
  ~40 PiB raw space
EB Storage Servers Intel GOLD series with PMEM
Data Handling and book-keeping software defined storage
No redundancy
Target BW 100GB/s in and 100GB/s out
WIP

## Slide 13: HLT2 Buffer Storage
Software defined storage Ceph
Erasure coding 8d+2p
12 OSD servers (60 disks @ 18TB)
CEPHFS native kernel integration
Target BW 10GB/s in and 10GB/s out
4000 clients writing in parallel
~ 16 clients/500 streams reading EOS exports

## Slide 14: HLT2 Storage Benchmarking
125 GB/s writing
110 GB/S reading
Performance
at 70% occupancy

## Slide 15: Core Infrastructure Business continuity
ECS
k8s
Computing nodes
Do we really
need backups?

## Slide 16: The Green Free Cooling
‘Outside’ Fans running 10 - 85%
Return Air
~40°C
~ 27°C
Supply Air
Cooling principle “indirect free air cooling” = Air/Air Heat exchanger

## Slide 17: Does it work? PUE ~ 1.04 @ 450kW

## Slide 18: Outside temperature

## Slide 19: Summary
LHCb can do and afford a full read-out at bunch-crossing rate
AMD Rome (PCIe Gen4) based servers make compact, very-high-I/O event-builder, connected with 200 Gb/s InfiniBand
Event-selection is entirely in software to maximize physics yield, increase the amount of data collected, flexibility and minimize cost
  Fingers crossed 
THANK YOU!