## Slide 1: Riunione di servizio per CIF
Emiliano Dané – 28/11/2022

## Slide 2
Inner System PP1 Manifold upgrade
Side A
Checked:
Pipes coordinates
Pipes diameters
Bending radius (2.5 times outer diam.)
Not final but realistic components (T, El. Breakes)
Distance between T, bendings and EB for the Welding Head for the pipe production
Assembly procedure
Everything is needed to be checked again
Do you plan to have some shieldings covering the part of stainless steel pipe? (from QL to EB)
Stainless Steel
Titanium

## Slide 3
Inner System piping components: T, El. Breakes
It should be possible to weld directly the T to the El. Breake.

## Slide 4
CABLES
CABLES
CABLES
More space for the welding head
90° degree rotated
No interference with cabling
Preliminary drawing
CG 4 -> 10
CG 7 -> 9
CG 2 -> 8
CG 8 -> 2
CG 2 -> 2
CG 4 -> 2
CG 4 -> 2
CG 8 -> 3
CG 8 -> 2
Outer Barrell
OLD Version

## Slide 5: Outer Barrell distribution New Version
Capillary manifolds distribution
New design capillary distribution
Special cap for pressure test
Protection of Capillaries
Shielding

## Slide 6: PP1 piping
SIDE A PP1 piping
End Cap Manifolds
Inner System Manifolds
Inner System Manifolds

## Slide 7: Test Camera Climatica
Nuovo Ingresso Aria Secca
Dew Point [°C]
Test sovrappressione
Test
temperatura
Fase di «lavaggio»
 | Dew Point (°C) | TCC (°C)
Lavaggio Durata: 3h | -30,5 | 21,5
 | -36,1 | 21,2
 | -39,4 | 21,1
 | -45,7 | 21,0
 | -51,1 | 20,9
 | -58,1 | 20,8
3h
Tempo (minuti) | DP (°C) | TCC (°C)
11:45 | -56,8 | 20
13:48 | -61,1 | 15
14:35 | -60,3 | 16
14:40 | -60,4 | 17
14:50 | -60,0 | 18
14:55 | -60,0 | 19
15:22 | -60,0 | 20
Test al variare della temperatura
TARGET
Autocalibrazione sensori