## Slide 1
Giorgio Baldinelli1
Francesco Bianchi 1, Manuela Boscolo 2, Filippo Bosi 3, Fabrizio Palla 3, Cristiano Turrioni 1
1INFN Sezione di Perugia, Italy
2INFN Laboratori Nazionali di Frascati (RM), Italy
3INFN Sezione di Pisa, Italy
Frascati, 16-17 November 2023

## Slide 2: The IDEA Concept
Silicon detectors for precision measurements
(vertex detector, silicon internal tracker)

## Slide 3: Overall Vertex layout
Total power ~120 W – Air cooled
Total weight ~230 grams
3 layers

## Slide 4
18 overlapping staves of double 16 modules each
Total weight ~150 grams
Power budget
~77 W
Layer 3

## Slide 5
APPROACH FOR THERMAL SIMULATIONS
Heat transfer through solid bodies and to the fluid (air) must be taken into account in the thermal model.
The geometric complexity of the structure and the small thickness of the parts are the most challenging aspects: simplifications of the model are needed.
Full model of the three layers

## Slide 6
APPROACH FOR THERMAL SIMULATIONS
Focus, at the moment, on Layer 3

## Slide 7
APPROACH FOR THERMAL SIMULATIONS
Extracting 40° sector (periodic)

## Slide 8
THERMAL SIMULATIONS
MODELS AND BOUNDARY CONDITIONS
Steady state conditions
Turbulent flow
Reynolds Average Navier Stokes (RANS) approach
Viscous model k-ω SST
Pressure based solver
No radiation heat exchange
….
Air at 15°C – 20 m/s
Pressure outlet
All walls adiabatic
Power generation in the silicon
More details on:
https://indico.cern.ch/event/1292318/contributions/5467218/attachments/2681519/4651774/Baldinelli%2010th%20of%20July%20rev%201.pdf

## Slide 9
3 mm diameter holes
6 mm diameter hole
Analysis of air cooling
Same inlet air speed: 20 m/s

## Slide 10
CASE 1: 3 mm diameter air inlet holes
GLOBAL TEMPERATURES
Tavg_modules = 40°C
Tmax_modules = 66°C
Tair_in = 15°C
Tair_out = 40°C
Vair_in = 20 m/s
Vair_avg = 0.99 m/s
THERMAL SIMULATIONS
Thermal figure of merit:
Modules maximum temperature – air inlet temperature
66.0-15.0 = 51.0°C
Linear behaviour with the inlet temperature

## Slide 11
CASE 2: 6 mm air inlet holes
GLOBAL TEMPERATURES
Tavg_modules = 25.5 °C
Tmax_modules = 32.9 °C
Tair_in = 15 °C
Tair_out = 20.8 °C
Vair_in = 20 m/s
Vair_avg = 3.28 m/s
THERMAL SIMULATIONS
Thermal figure of merit:
32.9-15.0 = 17.9°C
Linear behaviour with inlet temperature

## Slide 12
3 and 6 mm air inlet holes comparison (20 m/s)
GLOBAL TEMPERATURES
THERMAL SIMULATIONS
3 mm
6 mm

## Slide 13
3 and 6 mm air inlet holes comparison (20 m/s)
FLOW PATTERNS
THERMAL SIMULATIONS
3 mm diameter holes
6 mm diameter holes

## Slide 14
3 and 6 mm air inlet holes comparison (20 m/s)
FLOW PATTERNS
THERMAL SIMULATIONS
3 mm diameter holes
6 mm diameter holes

## Slide 15
3 and 6 mm air inlet holes comparison (20 m/s)
AIR SPEED
THERMAL SIMULATIONS
3 mm diameter holes
6 mm diameter holes

## Slide 16
3 and 6 mm air inlet holes comparison (20 m/s)
TURBULENT INTENSITY
THERMAL SIMULATIONS
3 mm diameter holes
6 mm diameter holes

## Slide 17
CASE 2: 6 mm air inlet holes (20 m/s)
TEMPERATURES
THERMAL SIMULATIONS

## Slide 18
EFFECT OF THE AIR SPEED
THERMAL SIMULATIONS
3 mm diameter holes
6 mm diameter hole
What is the influence of the air speed on the cooling performance, keeping constant all the other boundary conditions?
SIMULATIONS IMPLEMENTED AT:
10 m/s
20 m/s
30 m/s

## Slide 19
EFFECT OF THE AIR SPEED
THERMAL SIMULATIONS
Air inlet temperature = 15°C

## Slide 20
EFFECT OF THE AIR SPEED
THERMAL SIMULATIONS
Air inlet temperature = 15°C

## Slide 21
THERMAL SIMULATIONS
CONCLUSIONS AND FUTURE WORK
The holes diameter and the air inlet speed optimisation affent strongly the thermal field
of the modules.
An increase in air mass flow rate, turns to an obvious decrease of the maximum temperature of the modules, a plateau exists and it has been detected.
The model still needs improvement:
  Anisotropy of the materials
  Turbulent model
  Refinement of the boundary conditions
  Simulations of the three layers together.
Optimisation of the system: speed and temperature of air, proper direction of the inlet flow, materials,, change of gas, if needed, etc…).
Experimental validation of the simulations.
A parallel mechanical analysis is ongoing, with a particular focus on the vibrational point of view.