## Slide 1
Experimental verification of the vertex detector Air Cooling System
Gherardo Ammirabile
Filippo Bosi, Maurizio Massa , Andrea Moggi, Gabriele Balestri,
Fabrizio Palla
INFN Pisa
Pisa, FCC-ee vertex detector R&D workshop
31/10/2025

## Slide 2
INTRODUCTION
Requirements of the vertex detector
Current vertex layout
Inner vertex
Mockup of the vertex detector
  Experimental setup: compressed air system
      First test results
      Timeline for next steps
      Conclusions
Gherardo Ammirabile, INFN Pisa
FCC-ee vertex detector R&D workshop, Pisa 31/10/25

## Slide 3
Requirements of the vertex detector
Low
material budget
Structure
Fluids
Lightweight but rigid
Effective cooling system
P h y s y c s
E n g i n e e r i n g
In general:
Minimize the effect of material in front of the LumiCal (below 130 mrad)
Facilitate assembly, opening and maintenance operations
FCC-ee vertex detector R&D workshop, Pisa 31/10/25
Gherardo Ammirabile, INFN Pisa
see Armin Ilg talk

## Slide 4
Fluids
Heat load from the sensors:
  Inner Vertex (ARCADIA based): 50 mW/cm2
  Outer vertex and disks (ATLASPIX3 based): 100 mW/cm2
Radiation length:
  Density of the fluid
  Pipes material
  Distance from IP
Choice is based on:
WATER
AIR
WATER
AIR
FCC-ee vertex detector R&D workshop, Pisa 31/10/25
Gherardo Ammirabile, INFN Pisa
Sensors completely immersed in the fluid

## Slide 5
Current vertex layout
Outer vertex tracker:
ATLASPix3 based
Modules of pixel size
Intermediate barrel at 13 cm radius
Outer barrel at 31.5 cm radius
3 discs per side
Inner Vertex detector:
ARCADIA based
Modules of pixel size
3 barrel layers at
13.7, 23.7 and 34/35.6 mm radius
Gherardo Ammirabile, INFN Pisa
FCC-ee vertex detector R&D workshop, Pisa 31/10/25

## Slide 6
Layer 1:
15 staves of 6 modules each
Power budget ≈ 12 W
227.4 mm
13.7
Reticular lightweight support to provide stiffness:
Thin carbon fiber walls interleaved with Rohacell
2 buses (data and power) 1.8 mm wide and 250 μm thick
Layer 2:
24 staves of 10 modules each
Power budget ≈ 32 W
Layer 3:
36 staves of 16 modules each
Power budget ≈ 77 W
356.2 mm
23.7
549.4 mm
35.6
Inner vertex
Gherardo Ammirabile, INFN Pisa
FCC-ee vertex detector R&D workshop, Pisa 31/10/25

## Slide 7
Gherardo Ammirabile, INFN Pisa
Lower
Upper
With stave
R
E
S
U
L
T
Stave dimensions (mm) |  | 
 | H | W
Design | 10.5 | 1.4
Real | 10.8 | 2.6*
* increase in thickness of Rohacell (best compromise between cost & manufacturing)
W
H
Glue ~ 90 μm
CF strip = 360 μm
Brass strip = 50 μm
Heater = 150 μm
Mockup of the vertex detector
Silicon modules replaced by a brass strip with the same thickness = 50 μm
Thermal load created by a bonded heater
Shape to be optimized with Aeroelastic studies
Bonding tool
FCC-ee vertex detector R&D workshop, Pisa 31/10/25

## Slide 8
Layer 3
Layer 2
Layer 1
Bus
AIR
INLET
SUPPORT
AIR
OUTLET
SUPPORT
Bus
3 separated ducts one for each of the layers
Split support for assembly
Gherardo Ammirabile, INFN Pisa
1st test
60°
Support of the staves
Target: support & cool the silicon detectors
Result: 3D printed support with integrated air ducts
(High Temp Resin)
FCC-ee vertex detector R&D workshop, Pisa 31/10/25
Air ducts
Cables ducts

## Slide 9
Experimental setup to evaluate the effectiveness of air cooling
Compressed air system to define:
Flow rate needed to cool the detectors
Pressure drop in the central region
Temperature increase between inlet and outlet
First test on a 60° circular sector of layer 3 including five staves
Next test on the same circular sector with all three layers
Gherardo Ammirabile, INFN Pisa
FCC-ee vertex detector R&D workshop, Pisa 31/10/25

## Slide 10
Gherardo Ammirabile, INFN Pisa
Flowmeters
Absolute Pressure sensor
Temperature/Humidity sensor
Valve group
RTD
1600 mm
380 mm
Test section
Designed to:
Be adaptable
Be controlled
Allow CFD result verification
FCC-ee vertex detector R&D workshop, Pisa 31/10/25
6 bar
0.5 m3
Serbatoio
Settling chamber
Drier
Test section
H
E
A
T Exch
Diffuser

## Slide 11
Gherardo Ammirabile, INFN Pisa
Staves under thermal testing
6
5
Stave 6
Stave 5
Power density (sensor) = 50 mW/cm2
Total power (each stave) = 2.2 W
The Middle section has the highest temperature
(heat exchange at the ends with the support)
Without cooling > 65°C
With cooling < 40°C
Top view
First test: 60° angular sector of only layer 3
FCC-ee vertex detector R&D workshop, Pisa 31/10/25
Chart: T_air_in=22.5°C, Stave n°5
| 40.299999999999997 | 60 | 84 | 103.4 | 127 | 163
Middle | 40 | 35.6 | 32.3 | 30.9 | 30 | 28.9
In | 28.9 | 27.2 | 25.9 | 25.5 | 25.4 | 25.1
Out | 37.6 | 34.1 | 31.1 | 29.8 | 29 | 28
ΔT within the stave | 11.1 | 8.4 | 6.4 | 5.4 | 4.6 | 3.8
Chart: T_air_in=22.5°C, Stave n°6
| 40.299999999999997 | 60 | 84 | 103.4 | 127 | 163
Middle | 40.7 | 36.7 | 33.5 | 31.9 | 30.9 | 29.6
In | 29.6 | 27.5 | 25.9 | 25.5 | 25.3 | 25
Out | 38.4 | 34.8 | 31.6 | 30.3 | 29.4 | 28.4
ΔT within the stave | 11.1 | 9.2 | 7.6 | 6.4 | 5.6 | 4.6
ΔT~ 6 – 7 °C

## Slide 12
The air cooling system appears to be effective for the case of study but we need to:
Upgrade hydraulic tightness to decouple air flow paths from cable entry/exit routes
Evaluate the vibrations of the structure connected to the air flow
Gherardo Ammirabile, INFN Pisa
Consistent with the allowed ΔT values between sensors, it would be advisable to maintain low flow rates to avoid significant aeroelastic issues
(simulations in progress with INFN Perugia)
Chart: ΔP-Flow rate
| 40.299999999999997 | 60 | 84 | 103.4 | 127 | 163
Tin=22.5°C | 3 | 16 | 35 | 55 | 85 | 155
Chart: Internal diameter of inlet pipes 4 mm
| 40.299999999999997 | 60 | 84 | 103.4 | 127 | 163
V_test section | 1.0867 | 1.4128 | 1.9923 | 2.427 | 2.9342 | 3.876
V_inlet | 11.2812 | 14.6656 | 20.6823 | 25.1948 | 30.4594 | 40.2365
Voutlet | 3 | 3.9 | 5.5 | 6.7 | 8.1 | 10.7
FCC-ee vertex detector R&D workshop, Pisa 31/10/25
ΔT~ 6 – 7 °C
Air velocity inlet ~ 20-25 m/s
Air velocity middle (average) ~ 2-2.5 m/s
Air velocity outlet ~ 5-7 m/s

## Slide 13
Timeline for next steps:
Assembly on the same 60°angular sector of the staves of Layer 2 and Layer 1
Gherardo Ammirabile, INFN Pisa
Expected results: by the end of the year
Targets:
Flow rate to cool each layer
Pressure drop
Thermal connection between them
Details to study:
Air induced vibrations with optical instrument
Inlet shape:
Circular Slotted
60°
Staves:
5 for Layer 3
3 for Layer 2
2 for Layer 1
Advantage:
The compressed air system offers versatility, enabling specific testing for single and multi layer solution
FCC-ee vertex detector R&D workshop, Pisa 31/10/25

## Slide 14
Gherardo Ammirabile, INFN Pisa
FCC-ee vertex detector R&D workshop, Pisa 31/10/25
CONCLUSIONS:
The air cooling system seems to be
adequate for the case study
The compressed air system is stable and dynamic, allowing continuous testing for different solutions
It’s possible to control and monitor the properties of the air being introduced into the test section in terms of:
- Flow rate (Pressure)
- Humidity
- Temperature
The maximum flow rate required for cooling is determined by the vibration allowed by the structure

## Slide 15: Thank you for your attention!